| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check Border /Title block (Signatory initials, Revision Phrases, date in title block), Scale Bar, Stamp (review/approval/construction), North direction block matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Check Drawing limit, key plan, coordinates & adjacent sheet reference of the plan/view (Try to follow key plan as per piping layout key plan for easy of modeling and extraction of layout). |  |  |  |
|  | Check Drawing Scales, line, Text properties are followed as per project drafting philosophy / CAD manual and is mentioned in the drawing. If scale for detail view is different than drawing Scale then same is indicated in drawing Scale of frame as mentioned in title block. Check bar scale in line with drawing scale. |  |  |  |
|  | Ensure all symbols are as per legend sheet. All legends as per project / client standards. Centre line shall be indicated for trays. Cable tray / Trench sizes are mentioned. |  |  |  |
|  | Ensure that no abbreviations are used in drawing Title. Abbreviations if any are included in the legend part at the drawing. |  |  |  |
|  | Check proper tray supports (in instrumentation scope) are indicated on the drawing. Tray support numbering is as per project philosophy and is in-line with supports installation drawings. |  |  |  |
|  | Check Vessel/equipment numbers for major equipment are shown. Proper grid numbers for Pipe Rack columns are given. (Equipment no. and grid no of Structure / Pipe rack shown as per unit plot plan) |  |  |  |
|  | Check as a consistency check tray / trench routing drawing is checked with model for coverage of all trays / trenches, JB, Panel, Instrument locations. |  |  |  |
|  | Check cable routing drawing is checked with cable route section detail document (cable route index) for cable sections, tray numbers and cable numbers. Check tray / trench numbers, cable route section numbers are route repeated. Cable tray loading / sizing shall be reviewed considering the spare philosophy. Check all main cables are covered in cable route index. |  |  |  |
|  | Check sleeves are properly terminated till trenches & sleeve numbers / table are shown. Sleeve numbers as per numbering philosophy. |  |  |  |
|  | Check notes shown on drawing are relevant, and appropriately referenced. |  |  |  |
|  | Check holds if any are indicated on drawing, with proper HOLD clouds. |  |  |  |
|  | Check cross reference of all the applicable relevant drawings including civil / piping drawings are indicated in reference drawings List / notes. Wherever required applicable package vendor drawing reference is mentioned. |  |  |  |
|  | Check appropriate reference drawing (Piping Plot Plan, Electrical Trench layout in case of crossing etc.) to be added. |  |  |  |
|  | Check Electrical cable / pipe crossings are indicated with symbols on trench route. |  |  |  |
|  | Check Cross sectional views of instrument cable crossing with electrical cable / civil drainage / pipe in trench with minimum safe distance of appropriate segregation are shown in line with project / client std / requirement. |  |  |  |
|  | Check all cross sectional views of instrument cable duct bank with detailed dimensions are shown. Or civil drawing for duct bank reference no. are indicated. |  |  |  |
|  | Check removal of unnecessary part of back ground (piping / civil) drawing. For example, note number, hold, reference, sectional, views etc. |  |  |  |
|  | Ensure Drawing Title, Rev matches with TDR. Soft file name / path as per project specific requirement is mentioned in drawing. Approval category to be ensured. |  |  |  |
|  | Ensure wherever required for critical tray routing detail views are shown with proper details and dimensions. The arrow direction for cutting sections are properly indicated. |  |  |  |
|  | Ensure correct tray / trench / sleeve numbers are indicated as per project numbering philosophy. |  |  |  |
|  | Ensure changes wrt old revision of Drawing and client comments are indicated with proper cloud mark and rev. mark. |  |  |  |
|  | Ensure Key plan is uniform in all drawings. and hatched area shall be relevant with actual drawing. |  |  |  |
|  | Ensure Match Line coordinates are consistent with continuation drawings. |  |  |  |
|  | Ensure all the items (Instruments, Junction boxes, Air Panels, MCT, sleeves etc) as per project requirement are covered in cable routing drawing. |  |  |  |
|  | Ensure trench Entry / Exit points wrt. control room, substation or satellite room interfaced properly with civil for adequacy in MCT sizing, cutout sizing. In case cables are Lead Sheath type then cable bending radius shall be reviewed. |  |  |  |
|  | Ensure North / East coordinates or reference distances are mentioned at major tray / Trench bends. |  |  |  |
|  | Ensure Inst cable Road Crossings (IRC) concrete blocks designed as per guidelines agreed with Civil. Pipe sleeve sizing is reviewed. |  |  |  |
|  | Check tray / trench clashing in 2D soft file / 3D model with existing & new underground / above ground facilities of civil, piping, electrical, telecom. Check safe distance of trench with other facilities. |  |  |  |
|  | Ensure FGL, FFL and Platform elevation with proper symbol is indicated wherever required. |  |  |  |
|  | Ensure tray elevations are indicated for tray up / down. Proper symbol for tray up and down is shown. Wherever tray reducers are used tray sizes are indicated on both sides of reducers. |  |  |  |
|  | Ensure while deciding the Trench / Tray size, check cable segregation as per project requirement. 110 VDC cables shall run on separate tray or if in trench then minimum gap shall be maintain between 110 VDC cables and other Instrument signal cables. Minimum gap (as per project specification) shall be maintained between HV/LV cables and Instrument cables. |  |  |  |
|  | Ensure all sheets are available in the set of drawing before deliver. |  |  |  |
|  | Ensure issue IDC to electrical / piping / civil / telecom dept. Get their comments incorporated before issuing drawing. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |