| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check Border /Title block (Signatory initials, Revision Phrases, date in title block), Scale Bar, Stamp (review/approval/construction), North direction block matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Check Drawing limit, key plan, coordinates & adjacent sheet reference of the plan/view (try to follow key plan as per piping Layout key plan for case of modeling and extraction of layout. |  |  |  |
|  | Check changes wrt old revision of Drawing and clients comments are indicated with proper cloud mark. |  |  |  |
|  | Check Drawing Scales, Line, Text properties are followed as per project drafting philosophy / CAD manual and is mentioned in the drawing. If scales for Detail View is different than Drawing scale then same is indicated in Drawing scale of frame as mentioned in title block. |  |  |  |
|  | Ensure Drawing title, Rev matches with TDR. Soft file name / path as per project specific requirement is mention in Drawing. |  |  |  |
|  | Ensure notes shown on Drawing are relevant. |  |  |  |
|  | Ensure holds if any are indicated on drawing with proper cloud mark. |  |  |  |
|  | Ensure all control room / auxiliary equipments mention below are shown. 8.1. System: a) Consoles / Work-station / Hardwere console. b) Printers. c) Operator Furniture. d) Table Top items e) Marshalling / System cabinets. f) Server Cabinets. g) Power distribution board / cabinets h) Global Positioning System (GPS) / Weather / Air direction monitoring equipment. i) F&G, ESD Matrix / Mimic Panel. j) MOS console. k) CCTV. l) PAGA equipment m) AMADAS Console, Server. n) BFAS cabinet. o) IRP or IFB Cabinet. 8.2. Vendor Cabinets: a) BMS Cabinets for fired heater. b) Anti surge & Performance monitoring panel for Compressors. c) Active Magnetic bearing (AMB) cabinet for Turbo – Expander. d) Condition Monitoring Cabinets (Temperature & vibration monitoring). e) Flow Metering Cabinets. f) Corrosion Monitoring Cabinet All above equipments need to be cross checked with the cable block diagram / overall control system architecture diagram. |  |  |  |
|  | Ensure the dimensions (verify with final vendor prints for AFC issue) of all equipment are as per the information available from vendors. |  |  |  |
|  | Ensure the access requirements of the various cabinets (Front/rear/side) and space provision for the same. |  |  |  |
|  | Check the minimum distance requirements from the wall to the panels / cabinets as stipulated by the STD Specification / local regulations. Minimum distance between cabinets in two adjacent rows considering door opening or swing frame movement. |  |  |  |
|  | Ensure sufficient moving space is available for personnel and operator movements as per std Ergonomic design requirements specified in ISA / EEMUA with special Emphasis on the console degrees of alignment. |  |  |  |
|  | Check space of document storage cabinets, control room operator furniture such as table and chair, configuration tools such as lap top computers are reflected in Drawing. |  |  |  |
|  | Ensure the width and height of doors, corridor space and entry ramp are sufficient for moving the largest piece of equipment / crate. |  |  |  |
|  | Check if cavity floor is required or the flat level can be matched with the false floor height. Check if we can include the false floor matrix. |  |  |  |
|  | Check the false floor depth and false ceiling height are adequate to provide for under false floor cable routing, bending & clamping of all cables. Check requirements for anti static flooring. |  |  |  |
|  | Ensure the various cabinet are located in such a way that crossing of cables can be avoided to extent possible – for e.g. system cabinet and related marshalling cabinets can be located parallel to each other and also ensure system wise cabinets are aligned to the extent possible. |  |  |  |
|  | Ensure the most optimum location for cable entry ensuring that the entry is without hindrances outside the control room. Indicate the type of cable entry – such as pipe sleeves, cable trays, MCT, etc. and allow sufficient space for the cable entry & subsequent bending & clamping of cables. |  |  |  |
|  | Ensure that the distances between the cabinets, which are connected by serial link cables or prefab cables are within the distance limitation of the links. |  |  |  |
|  | Check sufficient space for future expansions – as far as possible system wise – in line with the spare philosophy. |  |  |  |
|  | Ensure optimum usage of space for locating equipment if the work involved is in an existing control room. |  |  |  |
|  | Ensure existing equipment in an existing control room in a faint shade or cloud the new equipment to be installed. |  |  |  |
|  | Check equipment to be demolished in an existing control room. |  |  |  |
|  | Check obstructions free air movement if the control room is to be provided with window air conditioners. |  |  |  |
|  | Check provision for cabling between equipment room / control room / HVAC room along with any fooling with floor beans. |  |  |  |
|  | Check co-ordinate location of the HVAC duct, light fixture, VESDA related tubing, smoke detector etc. |  |  |  |
|  | Check if there are any recommendation for the control room ergonomic study that need to be followed |  |  |  |
|  | Check emergency exits (door with push bar) double door airlock |  |  |  |
|  | Check location of earth bus bars and insert plates (if required) |  |  |  |
|  | Ensure cross reference of all the applicable relevant drawing is indicated in reference Drawings Lists / Notes. Wherever required applicable vendor drawing reference is mentioned. |  |  |  |
|  | Ensure that no abbreviations are used in Drawing Title. Abbreviations if any included in the legend past of the drawing. |  |  |  |
|  | Check IDC is issued to electrical / civil / telecom department. Get their comments incorporated before issuing drawing. Ensure I/P from Electrical / Piping / Civil / Telecom / HSE is available prior to IDC & post IDC comments are incorporated & signed off. |  |  |  |
|  | Check the location of electrical sockets in the room for the powering instrument items to be worked out and informed to electrical. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |