| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check Border /Title block (Signatory initials, Revision Phrases, date in title block), Stamp (review/approval/construction), North direction block matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Ensure Drawing Title, Rev matches with TDR. Soft file name/path as per project specific requirement is mentioned in drawing. Approval category to be ensured. Approval category to be ensured. |  |  |  |
|  | Check Drawing limit, key plan, coordinates & adjacent sheet reference of the plan/view (Try to follow key plan as per piping layout key plan for easy of modeling and extraction of layout). |  |  |  |
|  | Ensure changes wrt old revision of Drawing and clients comments are indicated with proper cloud mark and rev. mark. |  |  |  |
|  | Ensure Drawing Scales, line, text properties are followed as per project drafting philosophy / CAD manual and is mentioned in the drawing. If scale for detail view is different than Drawing Scale then same is indicated in Drawing Scale of frame as mentioned in title block. Check bar scale in line with drawing scale. |  |  |  |
|  | Ensure all symbols are as per Approved legend sheet. All legends as per project / client standards. (For symbol automatically generate from PDS/PPDMS during extraction of location layout give symbol file to PDS/PDMS administration for Macro script) |  |  |  |
|  | Check Match Line coordinates are consistent with continuation drawing. |  |  |  |
|  | Ensure Key Plan is uniform in all drawing and hatched area shall be relevant with actual drawing. |  |  |  |
|  | Check notes shown on drawing are relevant. |  |  |  |
|  | Ensure that no abbreviations are used in drawing Title. Abbreviations if any are included in the legend past of the drawing. |  |  |  |
|  | Check the elevation of all Instruments / Fire & Gas detectors wrt to the Finished Floor Level / Grade level / Platform level. |  |  |  |
|  | Check holds if any are indicated on drawing with proper cloud mark. |  |  |  |
|  | Check removal of unnecessary part of back ground (piping) drawing. For example, note number, hold, reference, sectional views, instrument tags etc (Applicable only in case of 2D dwgs). |  |  |  |
|  | Ensure all multiple sheets are available in the set of drawing before deliver. |  |  |  |
|  | Check Instrument symbols are aligned properly without any crossing of lines. |  |  |  |
|  | Check FGL, FFl and Platform elevation with proper symbol is indicated wherever required. |  |  |  |
|  | Ensure Vessel/equipment numbers for major equipments are shown. Proper grid numbers, essential dimensions for Pipe Rack columns/pipe rack number are given. |  |  |  |
|  | Ensure before extraction of Location layout from Model checks all model are lock for relevant area. Confirm with PDMS/PDS administration. |  |  |  |
|  | Ensure prior to start with editing (editing JB numbers, symbol representation etc) work on Mass annotated drawing, one set of original mass annotation copy shall be preserved. Final locations of instruments, Junction boxes, panels etc in final drawing are checked with original mass annotation copy. |  |  |  |
|  | Ensure Fire and Gas detector grouping shall be as per Fire Zone only. Should not club Detector of one zone and detectors of other zone in same junction box. |  |  |  |
|  | Check as a consistency check F&G location plan is checked with index and cable schedule. |  |  |  |
|  | Ensure Fire zone limit covers the tags pertaining to that zone only. |  |  |  |
|  | Ensure Orientation of F&G instrument is properly shown, and is consistent with F&G conceptual layout. e.g. For open path infra red gas detectors source and detectors source and detector shall be arranged properly, detection direction of UV/IR flame detector. And distance between the source and receiver shall be ascertained based on the selected instrument model. |  |  |  |
|  | Check whether sectional view of pit/platform with detectors/instruments is shown for more clarity. |  |  |  |
|  | Check in case of cable trays are shown in location layout, a) Horizontal tray elevations. b) Sizes of tray. c) Tray drop/rise elevations & relevant symbol. d) Reference distances of tray. e) Critical/overall tray routing detailed views are shown with proper details and dimensions. |  |  |  |
|  | Check VIEW TITLE (sectional plan with elevations/area name) |  |  |  |
|  | Check all multiple sheets are available in the set of drawing before delivery. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |