| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check Border /Title block (Signatory initials, Revision Phrases, date in title block), Stamp (review/approval/construction), North direction block matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Check changes wrt old revision of drawings and client comments are indicated with proper cloud mark, & Rev. mark. |  |  |  |
|  | Check Line, Text properties are followed as per project drafting philosophy / CAD manual. |  |  |  |
|  | Check drawing format as per Project / Client Standards / approval by lead engineer. |  |  |  |
|  | Check legends, abbreviations and notes shown on drawing are relevant and appropriately referenced. |  |  |  |
|  | Ensure Drawing Title, Rev matches with TDR. Soft file name / path as per project specific requirement are mentioned in drawing. Approval category to be ensured. |  |  |  |
|  | Check the drawing is sectionalized to show inputs, outputs and logic parts of the system correctly. Modularizing of relevant inputs, outputs and the logic area with respect to the process units. |  |  |  |
|  | Ensure all symbols are as per legend sheet. All legends as per project / client standards. |  |  |  |
|  | Ensure the legends and symbols used to represent are properly and correctly covered with clear identification and explanation. |  |  |  |
|  | Ensure coverage of all I/Os indicated on cause and effect drawings for process and plant start-up / shutdown narrative. Ensure coverage of all relevant I/O’s from F&G C&E drawings. These documents Shall also cover all package plants / package vendors. |  |  |  |
|  | Check maintenance overrides and start-up overrides as required are included. |  |  |  |
|  | Check notes shown on drawing are relevant. |  |  |  |
|  | Check holds if any are indicated on drawing. |  |  |  |
|  | Check cross reference of all the logic lines for clarity. |  |  |  |
|  | Ensure cross reference and continuation information of multiplied I/Os both incoming and outgoing are correct. |  |  |  |
|  | Check the correct loop description on the title block of each logic sheet. |  |  |  |
|  | Check correct loop tag number, service description and clear executive action details such as open, close, start, stop, etc. |  |  |  |
|  | Check that alarm for MOS/SOS/Input unhealthy, etc, are covered. |  |  |  |
|  | Check to indicate time delay (on delay, off delay, etc.) and reset as required. |  |  |  |
|  | Ensure the field instruments are identified clearly. |  |  |  |
|  | Check Agreement of initiator and actuations with cause and effects. |  |  |  |
|  | Check reference P&IDs and cause and effect drawing numbers. |  |  |  |
|  | Check mimic lamps and alarm outputs (hardwired and serial links) are properly indicated. |  |  |  |
|  | Check all hard wired, soft wired and serial link connections are represented. |  |  |  |
|  | Check whether items being modified as existing or new are indicated. |  |  |  |
|  | Check holds if any are indicated on drawing, with proper HOLD clouds. |  |  |  |
|  | Check that no abbreviations are used in Drawing title. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |