| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check Border /Title block (Signatory initials, Revision Phrases, date in title block), Stamp (review/approval/construction), North direction block matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Check changes wrt old revision of drawings and client comments are indicated with proper cloud mark, & Rev. mark. |  |  |  |
|  | Check text properties are followed as per project drafting philosophy / CAD manual. |  |  |  |
|  | Check cable schedule format as per Project / Client Standards / approval by lead engineer. |  |  |  |
|  | Check legends, abbreviations and notes are defined properly. |  |  |  |
|  | Check notes shown on document are relevant and appropriately referenced. |  |  |  |
|  | Check that no abbreviations are used in document title. Abbreviations if any are included in the legend part of the document. |  |  |  |
|  | Ensure Document Title, Rev matches with TDR. Soft file name / path as per project specific requirement are mentioned in document. Approval category to be ensured. |  |  |  |
|  | Ensure all applicable instruments in PIDs and all fire and gas detectors are covered and cross check with cable block diagram and instrument index. |  |  |  |
|  | Ensure requirement of package vendor, analyzers, Building fire alarm system and HVAC are included. |  |  |  |
|  | Ensure all interfaces with electrical system as well as cables between all control system as covered by the design basis are included. This shall cover all serial link cables or any specials also. |  |  |  |
|  | Check for consistency among Cable schedule, Cable block diagram and cable drum schedule. |  |  |  |
|  | Check that as a minimum reference drawing include cable block diagram, cable layout drawing, Instrument location drawing. |  |  |  |
|  | Check if availability of spares in each cable is as per the project specification. |  |  |  |
|  | Check holds if any are indicated on drawing. |  |  |  |
|  | Ensure all sheets are available in the set of documents before delivering. |  |  |  |
|  | Ensure that appropriate statement is made under “remark” column for instrument cables laid in electrical cables tray/trench or electrical cables laid in instrument cable tray/trench. |  |  |  |
|  | Ensure that cable length and end points of the cables match with the cable layout drawing. |  |  |  |
|  | Ensure that cables (for the same service) but which require diverse or separate routing as per the engineering specifications are correctly identified in the cable schedule indicating diverse route. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |