| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check border /Title block (Signatory initials, Revision Phrases, date in title block), Stamp (review/approval/construction), North direction block matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Ensure drawing Title, Rev matches with TDR. Soft file name/path as per project specific requirement is mentioned in drawing. Approval category to be ensured. |  |  |  |
|  | Check changes wrt old revision of Drawing and clients’ comments are indicated with proper cloud mark. |  |  |  |
|  | Ensure check line, text properties are followed as per project drafting philosophy / cad manual and is mentioned in the drawing. |  |  |  |
|  | Ensure all symbols are as per Approved legend sheet. All legends as per project / client standards. |  |  |  |
|  | Check notes shown on drawing are relevant. |  |  |  |
|  | Check holds if any are indicated on drawing with proper cloud mark. |  |  |  |
|  | Ensure that no abbreviations are used in Drg. Title. Abbreviations if any are included in the legend part of the drawing. |  |  |  |
|  | Check FGL, FFL and Platform with proper symbol is indicated wherever required. |  |  |  |
|  | Check for consistency between Installation drawing and P&ID, Hook-Up, Model. |  |  |  |
|  | Check all the items (Instruments, Junction Boxes, Air manifolds/main inst air take off (as required) Panels, etc) as per project requirements are covered in drawing. Including any loose supplied items on packages that are modeled. Equipment location plan / piping GID. |  |  |  |
|  | Check cross reference of all the applicable relevant drawing is indicated in reference Drgs. List/Notes. Wherever required applicable package vendor drawing reference is mentioned. Equipment Location Plan / Piping GID. |  |  |  |
|  | Check the elevation of all Instruments wrt to the Finished Floor level / Grade level / Platform level. |  |  |  |
|  | Ensure elevation of stanchion to be as per the hook-up drawing wise Above / below tapping point as per the service. |  |  |  |
|  | Check VIEW TITLE of the Details shown on the drawing. |  |  |  |
|  | Check all multiple sheets are available in the set of drawing before delivery. |  |  |  |
|  | Check the instrument vendor drawing to ensure that there is no conflict with respect to fixing instrument & canopy. |  |  |  |
|  | Ensure the requirement of Earth-boss or Earth-bond members on instrument/JB supports |  |  |  |
|  | Ensure that pedestals for structures with higher loads (like structure for Flame detectors) are provided with respect to civil design. |  |  |  |
|  | Ensure that any safety sign/description required by HSE in F&G device supports is provided as per HSE requirement. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |