| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check border /title block (Signatory initials, Revision phrases, date in title block), stamp (review/approval/construction). |  |  |  |
|  | Ensure drawing title, Rev matches with TDR. soft file name/path as per project specific requirement is mentioned in drawing. Approval category to be ensured. |  |  |  |
|  | Check changes wrt old revision of drawing and clients’ comments are indicated with proper cloud mark. |  |  |  |
|  | Ensure that the tag numbers are shown properly as per P&ID. |  |  |  |
|  | Ensure line, text properties are followed as per project drafting philosophy / cad manual and are mentioned in the drawing. |  |  |  |
|  | Ensure all symbols are as per approved legend sheet. All legends as per project / client standards. |  |  |  |
|  | Check notes shown on drawing are relevant. |  |  |  |
|  | Check holds if any are indicated on drawing with proper cloud mark. |  |  |  |
|  | Ensure that no abbreviations are used in Drg. title. Abbreviations if any are included in the legend part of the drawing. |  |  |  |
|  | Check for consistency between level sketches and P&ID. |  |  |  |
|  | Ensure all levels of level Instruments are as Per process data / Equipment data sheets issued by Process. |  |  |  |
|  | Ensure all nozzles C - C covers the various levels provided by process data. Also Ensure that the highest & lowest levels are within acceptable limits of transmitter calibrated range. |  |  |  |
|  | Ensure that the nozzle provided to sense the vapour pressure is correctly Located. ItShould be above the highest possible liquid level. |  |  |  |
|  | For columns & similar equipment ensure that the nozzle in vapour space corresponds to the liquid level for which the level is measured. |  |  |  |
|  | For interface level measurement by displacers ensure that the nozzles are so located that the displacers always remain fully immersed. |  |  |  |
|  | Check if there is a requirement in the project that, if there are more than one level instruments on a Equipment, all the high & low level nozzles are installed in the same elevation for the same level measurement. |  |  |  |
|  | Ensure that vapour Space tapping is not very near to schoepentoetor in a column. |  |  |  |
|  | For level measurement of the “Boot” of a vessel it is preferable to have the upper nozzle on the vessel & not on the boot. As the space between the upper part of “Boot” & vessel lower surface will be small, an upper nozzle on the boot could lead to problems. |  |  |  |
|  | For the level measurement of foam in skimmer ensure the dimension of the “bucket” or “Compartment” where the foam will be collected. The lower elevation of the level nozzle should be either slightly above or it the sense Elevation of the drain point provided to take out foam. |  |  |  |
|  | Wherever possible lower nozzle should be above the vessel lower than Line. |  |  |  |
|  | For radar type level instrument, nozzle stand-out & location shall be verified with the selected instrument vendor. |  |  |  |
|  | Ensure TL to TL of equipment is mentioned. |  |  |  |
|  | Check the equipment number on drawing is correct. |  |  |  |
|  | Ensure process conditions like Opr.press, Opr.temp, design pressure and design temp., are included. |  |  |  |
|  | Check the fluid in the equipment is mentioned in drawing. |  |  |  |
|  | Ensure the nozzle nos. & their sizes are correctly Identified. Nozzles nos. shall meet with P&IDs. |  |  |  |
|  | Ensure the visible Instrument ranges are mentioned in drawing. |  |  |  |
|  | Ensure the type of Instruments is mention correctly in the drawing. |  |  |  |
|  | Check the equipment I.D. and vessel trim specification is mentioned. |  |  |  |
|  | Check the P&ID no. & vessel trim Dwg.no is mentioned as reference drawing. |  |  |  |
|  | Check view TITLE of the details shown on the drawing. |  |  |  |
|  | Check all multiple sheets are available in the set of drawing before delivery. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |