| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Check Border /Title block (Signatory initials, Revision Phrases, date in title block), Stamp (review/approval/construction), matches with the project drafting specification and is consistent with the deliverables from other discipline. |  |  |  |
|  | Check changes wrt old revision of drawings and client comments are indicated with proper cloud mark, & Rev. mark. |  |  |  |
|  | Check Line, Text properties are followed as per project drafting philosophy / CAD manual. |  |  |  |
|  | Check drawing format as per Project / Client Standards / approval by lead engineer. |  |  |  |
|  | Check legends, abbreviations and notes shown on drawing are relevant and appropriately referenced. |  |  |  |
|  | Ensure Drawing Title, Rev matches with TDR. Soft file name / path as per project specific requirement are mentioned in drawing. Approval category to be ensured. |  |  |  |
|  | Ensure all symbols are as per legend sheet. All legends as per project / client standards. |  |  |  |
|  | Ensure the legends and symbols used to represent are properly and correctly covered with clear identification and explanation. |  |  |  |
|  | Check notes shown on drawing are relevant. |  |  |  |
|  | Check holds if any are indicated on drawing. |  |  |  |
|  | Check that no abbreviations are used in Drawing title. |  |  |  |
|  | Leave spare sheets between the sections (Notes, Legend sheet & Actual C&E) to accommodate the future additions of Fire & Gas zones. |  |  |  |
|  | A sheet (Notes & Legend) dedicatedly assigned for general notes explaining the concepts of Fire and Gas philosophy followed in the project and Legends describing the terminologies used inside the document. |  |  |  |
|  | A sheet showing complete gas detection with a table of all the gas zones including the gas detectors present in each Gas zone along with the alarms generated shall be prepared. |  |  |  |
|  | A sheet showing complete Fire detection with a table of all the Fire zones including the fire detectors present in each Fire zone along with the alarms generated shall be prepared. |  |  |  |
|  | In addition to the above, a sheet with table of Fire & Gas zones with the Sounders and Beacons connected to it shall be prepared. |  |  |  |
|  | The document number for individual sheets shall have incremental sheet nos. |  |  |  |
|  | Fire Zone C&E: (Each and Every sheet shall contain the following as a template) 1. Detectors belonging to the Fire Zone shall be grouped under type. 2. Separate columns for providing Rev No, Fire zone details, Voting, Location / Description, Interlock (UZ) Block and Notes shall be prepared. 3. The Local Panel and its associated tag numbers located in the respective Fire Zone shall be provided below the group of detectors. 4. Effects area shall have separate partition of columns for below mentioned signals - Intertrip signals (Confirmed Fire / Confirmed Gas) going to IPS / ESD System - HMI Alarms sent to DCS as serial signals - Signals going to F&G Matrix / Mimic Panel - Output signals going to Field i.e. to activate deluge system / signals to CCTV, PAGA, MOS Lamp etc. |  |  |  |
|  | The description for the initiators and the Final elements mentioned in the C&E shall match the description mentioned in I/O database. |  |  |  |
|  | Information related to Voting (1oo2 or 2oo3) shall be clearly indicated against the relevant initiators. |  |  |  |
|  | The sheet shall have enough space for notes (specific information) about the initiators / final elements, Fire and Gas detector layout number etc. |  |  |  |
|  | The “X" shall be correctly marked against the relevant initiators. |  |  |  |
|  | Any change in the "X" in the next revision shall be clouded / highlighted with the Revision no. marked in the specific column "REV". |  |  |  |
|  | Separate C&E shall be prepared for Building Fire Alarm System (BFAS). Its interaction in terms of intertrips with the Plant F&G system shall be elaborated. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |