| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Ensure the actions resulting from the 60% model review to be closed. Ensure the model shall be substantially complete, including Instrumentation. Final comments shall be made this stage. |  |  |  |
|  | Ensure that all tagged items inline/off line instruments are modeled (as per agenda fixed by model custodians for 90% review). |  |  |  |
|  | Ensure that all JBs along with support are modeled including packages/skid mounted. All package related JBs shall be marked some other colour than PIL supply JBs for easy identification of construction people. |  |  |  |
|  | Ensure that all local panels are modeled along with foundation. |  |  |  |
|  | Ensure the cable trays are supported properly includes tray fittings. |  |  |  |
|  | Ensure distances between Instrument trenches and electrical trenches are meeting the project specifications. |  |  |  |
|  | Ensure distance between instrument tray and electrical trays are meeting the project specifications. |  |  |  |
|  | Ensure distance between HOT pipes and tray/trenches are meeting the project specifications. |  |  |  |
|  | Check the JB installation is properly modeled for paved/unpaved area. |  |  |  |
|  | Check the Instrument/JB installation with operation/maintenance point of view. |  |  |  |
|  | Ensure Design basis/Company standards are strictly followed. |  |  |  |
|  | Check Instrument tag numbers has no errors. |  |  |  |
|  | Ensure straight length requirement as per vendor data. |  |  |  |
|  | Check orifice flanges installation as per services e.g. gas/vapor above tapping and liquid below tapings. |  |  |  |
|  | Check Level instrument (capillary) installation with respect to HP/LP requirements. |  |  |  |
|  | Check if Sunshades are modeled if required for instruments as per project specifications. |  |  |  |
|  | Ensure Analyzer panel installation along with distance required from sampling points. |  |  |  |
|  | Check orientation of actuators of Control valves, MOV, ON-OFF valves, etc. |  |  |  |
|  | Check the Valve sizes as per vendor approved drawings. |  |  |  |
|  | Check for Control room cable entries. |  |  |  |
|  | Check the Lighting requirement for local indicators. |  |  |  |
|  | Check any extra loop power indicator required apart from process requirement e.g. Instruments installed on high elevations or very low elevations. |  |  |  |
|  | Ensure the Accessibility for instruments and valves. |  |  |  |
|  | Check the Foundation for major supports. |  |  |  |
|  | Check Proper Tray fittings are modeled for perforated and ladder trays. |  |  |  |
|  | Check Distance between two trays (vertical and Horizontal). |  |  |  |
|  | Ensure the Loose supplied instruments by vendor are modeled in some other colour. |  |  |  |
|  | Ensure all F&G instruments are modeled as per HSE requirements. |  |  |  |
|  | Ensure the underground pipe sleeves are modeled wherever instrument trench is crossing with electrical cable trenches. |  |  |  |
|  | Ensure Duct banks are modeled for road and pipe trench crossings. |  |  |  |
|  | Check accessibility at Instrument/JB facing. |  |  |  |
|  | Check the cable tray routing for critical area like compressor shelters. |  |  |  |
|  | Check skid cable entries as per vendor and cable bending radius requirement. |  |  |  |
|  | Ensure cable tray sizing with respect to final cable count and IS/NIS philosophy. |  |  |  |
|  | Check cable tray routing at substation for instrument cables. |  |  |  |
|  | Check Electrical cable entry at instrument control room. |  |  |  |
|  | Check requirement of cable pulling pits. |  |  |  |
|  | Check directions and orientation of F&G instruments. |  |  |  |
|  | Check tray support arrangements at tanks and vessels. |  |  |  |
|  | Check Instrument installations on platforms are modeled as per approved installation drawings. |  |  |  |
|  | Check cable trench fouling with civil/piping supports. |  |  |  |
|  | Check Tray crossovers on pipe racks. |  |  |  |
|  | Check the Process tube routing in critical area. |  |  |  |
|  | Check Close drain requirement is properly modeled which is in piping scope. |  |  |  |
|  | Check any pit requirement for flow instrument. |  |  |  |
|  | Check Condensate/seal pots are modeled where ever required as per hook-up drawing. |  |  |  |
|  | Check air manifold or air header to be modeled as per project philosophy. |  |  |  |
|  | Ensure Volume bottle supports are modeled by others. |  |  |  |
|  | Check the Platform size around instrument. |  |  |  |
|  | Avoid Instrument installation on vibrating pipes. |  |  |  |
|  | Check Instrument installation comparing with wind direction for H2S area e.g. local ESD/test /reset push button stations. |  |  |  |
|  | Check ESD/reset push button locations. |  |  |  |
|  | Check constructability for trenches and u/g pipe sleeves. |  |  |  |
|  | Ensure control room equipment modeling with respect to project requirement. |  |  |  |
|  | Ensure availability of clear space for removable of instruments e.g. Pitot tubes and flow probes. |  |  |  |
|  | Check Extra supports are provided for big size valves by piping. |  |  |  |
|  | Check crane access or davit requirement for instrument drops from higher platforms |  |  |  |
|  | Check tank gauge dial size is quite enough with respect to the tank height to view the gauge from grade. |  |  |  |
|  | Check installation of float and tape gauges |  |  |  |
|  | Check installation of Linear heat detector cables. |  |  |  |
|  | Check piping nozzle / flange sizes for instrument connection. |  |  |  |
|  | Ensure the accessibility for tank instruments. |  |  |  |
|  | Check requirement of fireproofing for inline instruments. |  |  |  |
|  | Check air coolers cable tray routes. |  |  |  |
|  | Check underground conduit requirements for local instruments. |  |  |  |
|  | Check tapping availability for remote instruments. |  |  |  |
|  | Check for mobile trolley/stool requirements for inaccessible instruments. |  |  |  |
|  | Check Sounders and Beacons orientations and their supports height. |  |  |  |
|  | Ensure that Remote mounted Instruments & Junction boxes are not installed in access ways. |  |  |  |
|  | Check Local panels cable entry as per vendor data. |  |  |  |
|  | Check Cable route markers for trenches are modeled. |  |  |  |
|  | Check Built-up trenches width and depth. |  |  |  |
|  | Check any scope of Telecom dept. |  |  |  |
|  | Check Cable entry/pipe sleeves built-up trenches requirement around skid/shelters e.g. compressors and pumps. |  |  |  |
|  | Check Line of sight detector height and beam. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |