| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | Checks For Design: |  |  |  |
|  | Comply with Appropriate codes and standards. |  |  |  |
|  | Design complies with CDM Regulation. |  |  |  |
|  | Design Complies with project HSE Requirements. |  |  |  |
|  | Design complies with Design Basis & Project Specifications. |  |  |  |
|  | Whether “Spatial Separation” or distance criterion of the codes and standards have been observed in the 3D Model. |  |  |  |
|  | Checks For Accessibility/ Removal: |  |  |  |
|  | Accessibility checked as per Project Specification “Plant Layout & piping Design”. |  |  |  |
|  | Adequate consideration has been given to equipment removal paths/fork lift access aisles. |  |  |  |
|  | Equipment Layout have been reviewed for pull space, operator access and maintenance requirements. |  |  |  |
|  | Equipment is arranged such that personnel access to inspection ports and instruments minimize the need for ladders, catwalks and platforms. |  |  |  |
|  | Other equipment, piping, walls, columns or other plant features do not obstruct equipment man ways (especially for tanks). |  |  |  |
|  | Equipment is arranged to minimize the number of platforms required for operation and maintenance. |  |  |  |
|  | Equipment is arranged such that adequate clearance exists for the maintenance and removal of rotors from fans, blowers etc. (including the installation of temporary rigging beams, hoists, chain falls, etc.) |  |  |  |
|  | Requirements for equipment removal hatches and construction opening in floors, walls and roofs have been identified and shown. |  |  |  |
|  | Checks For Hoist/Crane/Monorail Requirement: |  |  |  |
|  | Crane hook limits have been considered when setting crane rail elevations. |  |  |  |
|  | The bottom of monorails/ hoists is not lower than the usable openings of roll-up doors, forklift access aisles etc. |  |  |  |
|  | Hoist hook limits have been considered when setting monorail elevations. |  |  |  |
|  | When required, equipment pulling posts and rails have been provided. |  |  |  |
|  | Monorails and/or facilities for temporary rigging have been considered |  |  |  |
|  | Checks For Piping Connected to Equipment: |  |  |  |
|  | Piping corridors have been established, where possible, to facilitate the use of racks and/or gang hangers. |  |  |  |
|  | Equipment is arranged to optimize piping layout. |  |  |  |
|  | Vendor trim piping around equipment is put in the model. |  |  |  |
|  | Equipment is arranged so that personnel access/ ingress paths are free from hazards posed by blowout panels, rupture discs and relief valve discharge stacks. |  |  |  |
|  | Equipment is arranged such that piping in gravity / atmospheric services do not have pockets or conditions of reverse slope. |  |  |  |
|  | Checks For Lay Down Space: |  |  |  |
|  | Adequate lay down areas is provided for use with cranes, gantries and monorails. |  |  |  |
|  | In multi-level structures, designated equipment dropdown areas have been identified and provided. |  |  |  |
|  | Checks For Code/ Specific Requirements: |  |  |  |
|  | Where required, eyewash/ safety showers are located within travel distances specified by the applicable design guidelines, codes and standards. |  |  |  |
|  | Where required, fire protection system deluge valve, hose racks, portable carbon dioxide equipment etc. have been located in accordance with applicable design guidelines, codes and standards. |  |  |  |
|  | Underside of equipment base plates is 200mm above high point of paving or FFL. |  |  |  |
|  | Where applicable, large filters, strainers etc. shall be located above drainage trenches or with in curbed areas to contain spillage during cartridge/ element replacement operations. |  |  |  |
|  | Where applicable, fuel unloading facilities, storage tanks etc. shall be enclosed with bunds, dykes and / or curbs. |  |  |  |
|  | Fuel system day tanks located outdoors shall be provided with sunshades when required by project specifications etc. |  |  |  |
|  | At truck unloading facilities, the dimensions of vehicles being used have been verified to ensure that proper vertical clearances, width, and turning radii have been considered. |  |  |  |
|  | Stairs ladders, catwalks and platforms comply with applicable design guides and codes. |  |  |  |
|  | General Checks: |  |  |  |
|  | Equipment footprints/ outline represent, to the extent possible, the actual dimensions and geometry as depicted on supplier/ vendor drawings. |  |  |  |
|  | Equipment is arranged such that HVAC system louvers, supply and exhaust fans are not obstructed by cable trays, piping, building steel, etc. |  |  |  |
|  | Equipment is arranged such that air intake grilles, exhaust fans and filter pull spaces are not obstructed at air-cooled pump motors etc. |  |  |  |
|  | Spacing between and around pumps, heat exchangers, tanks etc. adequately consider the area required for piping, pipe supports, cable tray, conduit, instrument stands etc. |  |  |  |
|  | Pumps and tanks are arranged to minimize the length of suction lines while avoiding high points and pockets. |  |  |  |
|  | Sumps are arranged such that connecting piping is not normally flooded with sump contents. |  |  |  |
|  | Compressors shall be located such that the possible induction of dust and potentially explosive gases are avoided. |  |  |  |
|  | Consideration has been given to the transmission of compressor vibration to the structure when choosing equipment location (including the installation of independent foundations). |  |  |  |
|  | Consideration has been given to the transmission of compressor vibration to adjacent control panels/ stations when choosing equipment location. |  |  |  |
|  | All cable trays of 150mm and above and HVAC ductwork have been indicated. |  |  |  |
|  | Door sizes and locations shown are based on standard sizes. |  |  |  |
|  | Equipment labels and tag numbers are shown in the model. |  |  |  |
|  | Annotation of equipment no. & name, building name, lay down area, ponds, sumps, containment areas etc. done. |  |  |  |
|  | Parking, Traffic barriers etc. as applicable |  |  |  |
|  | Dyke, bunds, curb are shown |  |  |  |
|  | First aid equipment as applicable with location shown. |  |  |  |
|  | Rescue equipment as applicable with location shown. |  |  |  |
|  | Safety signs shown. |  |  |  |
|  | Plant North; True North, Prevailing wind direction shown. |  |  |  |
|  | Major oil/ Gas pipeline & Interfacing with Pipeline corridor as applicable shown. |  |  |  |
|  | Anchor bolts are shown. |  |  |  |
|  | Checks For Fire Protection System: |  |  |  |
|  | Fire Water piping ring with location shown |  |  |  |
|  | Hydrants & monitors with location shown |  |  |  |
|  | Deluge & Sprinkler system with location shown |  |  |  |
|  | Fixed Fire Protection system – Dry Powder, Foam, Halon and CO2 with location shown. |  |  |  |
|  | Hose reels with location shown. |  |  |  |
|  | Checks For Piping/Instrumentation & Electrical: |  |  |  |
|  | All piping of sizes 1 ½ & above and all process critical lines are shown. |  |  |  |
|  | Valves & Instrumentation within 1830mm of floor if not whether appropriate access to valve such as platform has been considered and shown. |  |  |  |
|  | Accessibility checked as per Project Specification “Plant Layout & Piping Design” |  |  |  |
|  | Piping after insulation is outside the walkway access area. |  |  |  |
|  | Basket removal space for strainer available |  |  |  |
|  | Piping after insulation is outside the equipment maintenance access area. |  |  |  |
|  | Design of Pipe Routing carried out as per Project specification “Plant layout & Piping Design” |  |  |  |
|  | Terminal Point location, TP number and detail (Welded, flanges (RF or FF), screw etc.) are shown. |  |  |  |
|  | Equipment with terminal point correctly modelled. |  |  |  |
|  | Terminal number (Sequence of equipment A or B) and description is correct. |  |  |  |
|  | Flow Configurations (Physicalized). |  |  |  |
|  | Line Size and line number as per P&ID number. |  |  |  |
|  | Pipe Class. |  |  |  |
|  | All inline items as per P&ID shown. |  |  |  |
|  | Vents & drains are marked in the P&ID copy and shown in Model. |  |  |  |
|  | Flow Arrow’s correctness. |  |  |  |
|  | Supports are marked. |  |  |  |
|  | Coating/ Wrapping Requirement if any for underground metal pipe is indicated. |  |  |  |
|  | Interference Check done and reviewed. |  |  |  |
|  | Wall and floor penetrations are correctly depicted |  |  |  |
|  | Removable spools are provided to facilitate equipment maintenance/ removal. |  |  |  |
|  | Upstream/ downstream straight pipe requirements at butterfly valves, control valves, check valve, flow elements, flow meters, pump suction & discharge nozzles etc. are satisfied. |  |  |  |
|  | Heat tracing requirement (If any) is indicated. |  |  |  |
|  | PSV outlet lines are self-draining to flare header |  |  |  |
|  | Lines are sloped as designated on P&ID. |  |  |  |
|  | Vapor/ two-phase lines checked for pockets. |  |  |  |
|  | Two-phase lines are identified and appropriately designed. |  |  |  |
|  | Lines checked for flexibility to install blinds or spacer provided. |  |  |  |
|  | All Instrument/ Electrical Main & Branch Cable Trays shown. |  |  |  |
|  | Security Fence is shown. |  |  |  |
|  | Security Wall is shown. |  |  |  |
|  | Access/ Emergency Exit Gates are shown. |  |  |  |
|  | Barriers |  |  |  |
|  | Parking areas are shown |  |  |  |
|  | Roads (On Plot Only) are shown. |  |  |  |
|  | All Buildings (As A Block Outline Only) are shown |  |  |  |
|  | All Shelters (Complete Modeling with Columns, Beams, Sheeting Etc. (Other Steel and Bracing’s Only When Obstruction with Piping Can Be Expected) are shown. |  |  |  |
|  | Pig Protection Berm is shown. |  |  |  |
|  | All Foundation Including Footing/ Piling Wherever Applicable (Equipment, Pipe Support, Platform Etc.) are shown. |  |  |  |
|  | Dykes, Curb Walls, Bund Walls, Fire Separation Walls etc. are shown. |  |  |  |
|  | Valve Pits, Sumps, Catch Basins and Trenches, Culverts Any Other Pits etc. are shown. |  |  |  |
|  | Underground Sewer Piping is shown. |  |  |  |
|  | Storm Retention Pond is shown. |  |  |  |
|  | Platforms, Crossovers, Ladders, Stairways, Walkways Along with Associated Structural Steel. (Only Outline Including Hand railing, Toe plates Etc. for Representation Only) are shown. |  |  |  |
|  | All Paving, Hard Standing etc. are shown. |  |  |  |
|  | Septic Tank (As a Block) is shown. |  |  |  |
|  | All Secondary Pipe Supports are shown. |  |  |  |
|  | Pipe Rack (With Fireproofing if Applicable), Pipe Sleepers are shown. |  |  |  |
|  | Lifting Devices Crane/ Trolley Beams are shown. |  |  |  |
|  | All Mechanical Equipment- Static & Rotary. (Outline Including Nozzles & Vessel Trims.) are shown. |  |  |  |
|  | Flare And Stack are shown |  |  |  |
|  | All Package Units (As A Block Only with Limited Details) are shown. |  |  |  |
|  | All Access ways, Lay down areas, Removal, Maintenance & Operating Spaces, Escape ways etc. are shown. |  |  |  |
|  | Sample Cabinet and coolers are shown. |  |  |  |
|  | Cathodic Protection Rectifier as a Block is shown. |  |  |  |
|  | Electrical Power Generation Package as a Block is shown. |  |  |  |
|  | Electrical Main Cable Trays of 150 Mm Above is shown. |  |  |  |
|  | Underground Electrical Cable Trenches are shown. |  |  |  |
|  | Underground Electrical Conduits (Where Crossing is Expected) are shown. |  |  |  |
|  | Electrical transformers as a block is shown. Bus duct between Generator and the Switchboard are shown. |  |  |  |
|  | Electrical Panel, Junction Boxes, Push Button stations are shown. |  |  |  |
|  | Lighting Poles/ Fixtures etc. are shown. |  |  |  |
|  | CCTV is shown. |  |  |  |
|  | Instrument Main & Branch Cable Trays of 150 Mm And Above, Trenches, Junction Boxes, Transmitter Boxes etc. are shown. |  |  |  |
|  | Instrument Support Stands are shown. |  |  |  |
|  | Instruments (Not On Piping) are shown. |  |  |  |
|  | Shelters for Instruments are shown. |  |  |  |
|  | Detection Equipment are shown. |  |  |  |
|  | Instrument Local Control Panels, Shelters, Analyzer Houses etc. are shown. |  |  |  |
|  | Checks For Valves including Control Valves: |  |  |  |
|  | End to end dimension/ End type (Flanged/ Welded/ Screwed). |  |  |  |
|  | Valve correctly modelled with actuator or other details. |  |  |  |
|  | Valve orientations. |  |  |  |
|  | Gear Operator Orientation. |  |  |  |
|  | Valve Rating. |  |  |  |
|  | Checks For Vent and Drains/ Instrument taps: |  |  |  |
|  | All high point drains/ vents are added. |  |  |  |
|  | Instrument taps are shown with correct orientation and tag number. |  |  |  |
|  | Instrument tap sizes are correct. |  |  |  |
|  | Orifice flange/ flow meter has instrument tap orientation marked –up. |  |  |  |
|  | Location of instrument support stands (not – in-line instruments). |  |  |  |
|  | Routing of branch cable trays to the instrument and support for the same. |  |  |  |
|  | Instrument tubing routing and supports in critical congested areas are shown. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |

ANNEXURE – WORKSHEET FOR 3D MODEL REVIEW

| S. No. | Description | Line/Eqpt No | Comment | By | Action | By |
| --- | --- | --- | --- | --- | --- | --- |