| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | 25% Extra space provided for future expansion |  |  |  |
|  | Minimum 3* Meters clearance provided below Units Pipe racks not crossing any roads. |  |  |  |
|  | Minimum 2.2* Meters clearance provided below offsite pipe racks not crossing any roads. (Only for Walking below). |  |  |  |
|  | 7* Meters clearance provided for main road |  |  |  |
|  | 6* Meters clearance provided for Secondary Road. |  |  |  |
|  | Water lines more than 30” not routed above rack |  |  |  |
|  | Instrumentation and electrical cable trays located on top tier. |  |  |  |
|  | Process lines located on bottom tier as far as possible. |  |  |  |
|  | Utility lines and hot process lines located on upper tier. |  |  |  |
|  | Bigger size lines kept near rack columns. |  |  |  |
|  | Minimum spacing between pipes based on bigger size flange. |  |  |  |
|  | Thermal expansion at bends, branches taken into consideration for pipe spacing |  |  |  |
|  | Anchors in pipes at the anchor bay if such bay is provided |  |  |  |
|  | Anchors in pipes at the anchor bay if such bay is provided |  |  |  |
|  | Orifice meter runs are near the columns for access by portable ladder. |  |  |  |
|  | Lines requiring thermal loops are near the edge of rack. |  |  |  |
|  | Small bore line size increased to 2’’on rack. |  |  |  |
|  | Fire proofing provided for pipe rack. |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |