| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | The kW rating of the motors is checked from the latest load list. |  |  |  |
|  | The load analysis is done to check whether the transformer size is adequate or not. |  |  |  |
|  | The rating of SFU, MCB, MCCB, MPCB, relays etc., are checked with respect to Type-2 Coordination/Client Specification/ Relevant Standards Applicable. |  |  |  |
|  | In case the equipment or feeder rating not finalized, a note stating that “The motor feeder ratings is tentative; subject to or feeder finalization of change based on finalized mechanical equipment rating” shall be mentioned. |  |  |  |
|  | All hold / tentative points and client’s comments to be checked during revision. |  |  |  |
|  | All revised points of SLD shall be clouded with revision marked. |  |  |  |
|  | Drawing numbers and revisions shall be as per the document schedule in wrench. |  |  |  |
|  | Cable sizes, type and number of runs and type of starting shall be available in SLD. |  |  |  |
|  | To ensure all the electrical equipment as per equipment list are covered in SLD. |  |  |  |
|  | "In the notes of SLD, the following points are to be covered. (a) Details of features for ACB, MCCB, MPCB, SFU etc to be mentioned. (b) Motor feeders shall have provision for motor space heaters if mentioned in spec. (c) Relays shall be shown as applicable |  |  |  |
|  | Title block shall be as per project requirement. |  |  |  |
|  | In case contract specification legends is not available standard legends has to be followed. |  |  |  |
|  | Check the system voltage, frequency, phase, fault current and fault duration withstand time |  |  |  |
|  | Have the individual switchgear / PMC/MCC/MLDB/MADB/its distribution been identified & the substation /switchgear room location checked? |  |  |  |
|  | Have the instrumentation / instrument power supply requirements plus others disciplines requirements ( like UPS, Battery Charger, Rectifier …etc been checked? |  |  |  |
|  | Protection and metering – (CT & PT) specified correctly like (ratio, accuracy, class, connections, burden …etc. |  |  |  |
|  | Are feeder and equipment relays specified correctly including proper code (ANIS/IEC) |  |  |  |
|  | All notes on design basis & control logic / scheme written properly? |  |  |  |
|  | Have the equipment been identified the number and their ratings checked. |  |  |  |
|  | Protection device & description been checked? |  |  |  |
|  | Have the checked for electrical & mechanical operation and further control process requirement have been done. |  |  |  |
|  | Coordination with other system for interlocking. Shutdown sequences and other function been checked? |  |  |  |
|  | Has the agreed area responsibility for corrective operations & break point been taken care? |  |  |  |
|  | Key single line diagram, covering entire plant power supply distribution scheme been provided? |  |  |  |
|  | Single line diagram for HT panel and its distribution which covers total HT panel requirements, type of operations, upstream and down Stream. |  |  |  |
|  | Single Line drawings provided PMCC been provided? |  |  |  |
|  | Single Line drawings provided each MCC had been provided? |  |  |  |
|  | Single line drawings for ACB been provided? |  |  |  |
|  | Single line drawings for MLDB been provided? |  |  |  |
|  | Single line drawings for DCDB been provided? |  |  |  |
|  | Single line drawings for UPS been provided |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |