| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | The rating of the motors to be checked from the latest driven equipment data sheet. |  |  |  |
|  | The motor parameters to be selected with respect to efficiency class (IE1/IE2/IE3) of the motor as per project requirements. |  |  |  |
|  | The instruments load details should also be considered. |  |  |  |
|  | In case the motor equipment or feeder rating not finalized, a note stating that, “The motor feeder rating is tentative; subject to change based on final mechanical equipment rating” shall ne mentioned is the notes. |  |  |  |
|  | BKW, KW, rpm, Type of Starting and Mounting to be crosschecked with mechanical driven equipment data sheet. |  |  |  |
|  | Quantity of the drives to be checked with the latest P&I D. |  |  |  |
|  | All tentative / hold points and client’s comments to be checked during revision. |  |  |  |
|  | All revision points should be clouded with revision mark. |  |  |  |
|  | Drawing number, Description, Approval Category and revision etc. as per the document schedule |  |  |  |
|  | Requirement of Ventilation System, Air Conditioning System, Lighting Distribution System, Power Distribution System and Air-Exhaust System, Hoist and EOT crane. |  |  |  |
|  | Power Supply for Auxiliary Loads such as Actuator DBs, Space Heaters, Plant Maintenance System (Welding Sockets etc.) |  |  |  |
|  | Dewatering Pumps, Portable pumps, portable actuators. etc., to be checked properly. |  |  |  |
|  | For non-process plant admin building, canteen, guard room, temporary office, workshop, staff quarters and any special requirements |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |