| Project name : |  |  |
| --- | --- | --- |
| Project No.: |  | Tag No.: |
| Document No.: | REV. : | Date : |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | General: |  |  |  |
|  | Heat Duty, MM kcal/hr |  |  |  |
|  | Surface Area, m2 |  |  |  |
|  | - Finned area (extended area) |  |  |  |
|  | - Bare tube area |  |  |  |
|  | Design Margin on Area, (% overdesign) |  |  |  |
|  | Overall HT coefficient, kcal/hr m2 oC |  |  |  |
|  | Mean Temp Diff, oC (EMTD) |  |  |  |
|  | Fluid, Tube side |  |  |  |
|  | Allowable / Actual Pressure drop, Tube side, kg/cm2 |  |  |  |
|  | Pressure drop, Airside, mm H2O |  |  |  |
|  | MOC, Tube / Fin |  |  |  |
|  | Fouling Factor, Tube, hr m2 oC / kcal |  |  |  |
|  | Fouling Factor, Air, hr m2 oC / kcal |  |  |  |
|  | Check that all the process conditions are taken care in the output of the designed heat exchanger |  |  |  |
|  | Design includes all the applicable sizing cases, summer/ winter etc. |  |  |  |
|  | Approach temp between process temp and inlet air temp should not be less than 5.6 oC |  |  |  |
|  | Design air inlet temp is so chosen that the ambient air temp will fall below this temp. 95% of the time |  |  |  |
|  | Check that the outlet air temperature is not too high to affect the personnel safety |  |  |  |
|  | Tube side velocities |  |  |  |
|  | Unit Geometry: |  |  |  |
|  | No. of bundles per bay. |  |  |  |
|  | Bundle width |  |  |  |
|  | Tube and fin Geometry: |  |  |  |
|  | Check that min 1" tube od is selected |  |  |  |
|  | Check that the standard tube length is selected |  |  |  |
|  | Check that the standard fin height is selected |  |  |  |
|  | Check that standard fin density is selected |  |  |  |
|  | Check that optimum tube rows are used in the design |  |  |  |
|  | Check that proper tube type is selected in case of fluid inlet / outlet temp difference is greater than 93oC |  |  |  |
|  | For condenser applications, allocate more tube rows for vapor region |  |  |  |
|  | Nozzle Pressure drops, % |  |  |  |
|  | Fan Geometry: |  |  |  |
|  | Fan ring type |  |  |  |
|  | Ensure that the fan diameter is not more than 14 ft |  |  |  |
|  | Ensure that the ratio of fan area / bundle face area is min 40% |  |  |  |
|  | Ensure that the fan driver power is not greater than 22 KW. |  |  |  |
|  | Ensure that the fans are not overlapped or outside the length of the tube |  |  |  |
|  | Ensure that the face velocity is not greater than 4.1 m/s |  |  |  |

Notes:

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |