| Project name: |  |  |
| --- | --- | --- |
| Equipment Name: |  | Tag No.: |
| Document No.: | REV.: | Date: |

| S. No. | Check Items | Check |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | YES | NO |  |
|  | For consistency check, Civil foundation drawing shall be checked w.r.t: a) Vendor's Template Drawing and b) Load data |  |  |  |
|  | Check and ensure that foot print dimensions and anchor bolt locations are matching between final Vendor GAD and IFC foundation drawing. |  |  |  |
|  | Check consistency of weights shown in Vendor GAD / Foundation drawing vis a vis vendor datasheet, Vendor calculation sheets, sub-vendor document such as Auxiliary Equipment Vendor drawings etc. (Vendor's generally miss to add the correct weight of the bought out/ Sub ordered items) |  |  |  |
|  | Carry out assessment of baseplate weight based on the structural beam size, lengths (weight / meter) basis. *Challenge the Vendor data if found not correct and ascertain the load data before IFC release. |  |  |  |
|  | Check and ensure that vendor skid weight includes piping/valves, JBs/cable trays, platforms/walkways, hot/cold insulation etc. |  |  |  |
|  | Check the total weight and assess its accuracy considering the above. Compare with other past project data through MCMS |  |  |  |
|  | Check and confirm the Top of Concrete (TOC) dimension, the north direction and at least one of the reference points (for example a pump discharge centerline or Vessel inlet nozzle). For Static Equipment, it is also important to check the Nozzle orientation |  |  |  |
|  | Check the anchor bolt BOQ in civil foundation drawing for size, type and scope. Anchor bolt type, quantity, depth of penetration in concrete and projection to be checked and compared between both the drawings. Do consistency check, if anchor bolt details are duplicated in various document or on various pages of same document. |  |  |  |
|  | Check the clearance between the holes in the base frame and the anchor bolt diameter. This is particularly important if the anchor bolts are pre cast. Should be at least 4 mm for bolts less than 27 mm Dia and 6 mm for bolts above 27 mm Dia. |  |  |  |
|  | If there is a vendor supplied sole plate, please ensure that it is shown in Civil Foundation drawing and the TOC dimensions are adjusted accordingly. |  |  |  |
|  | Check the extent of grout and grout thickness in both vendor and civil foundation drawing. In case of Rotating Equipment, if full under grouting is not being done, there should be provision for pouring grout through holes in base frame. |  |  |  |
|  | For Rotating Equipment where the driven and driver Equipment are mounted on separate foundations, it is very important to check and reconfirm the Distance Between Shaft Ends (DBSE), the TOC dimension of both equipment separately, and reconfirm the Centerline height. |  |  |  |
|  | Check/Reconfirm the sleeve size & location for HT power cables & Instrument cables (when required) on the civil drawings which are to be casted in the concrete. |  |  |  |
|  | For pre cast anchor Bolts, it is very important that the equipment baseplate manufacturing tolerances are smaller than Civil foundation tolerances. Even when the anchor bolts have sleeves, still the Bolts cannot be moved by more than 3-4 mm. |  |  |  |
|  | Check the equipment slope and reference W.P. (Working Point) |  |  |  |
|  | Check the Fixed saddle and Sliding saddle locations. |  |  |  |
|  | Ensure to straddle anchor bolt locations w.r.t N-S centerline. |  |  |  |
|  | When the equipment or its part is projected below its support leg or saddle, verify its fouling with concrete pedestals (like boot in horizontal vessels, air plenum & burner assembly in heater/incinerator, etc.,) |  |  |  |
|  | Verify fouling of foundations below ground, even though it clears each other above ground. (Especially for multi skid items, equipment coming close to pipe racks/technological structures) |  |  |  |
|  | For Package items, check locations of auxiliary items for their fouling with electrical trenches, instrumentation trenches, fire water piping/trenches, open trenches for rain water, etc., (e.g. stairway leg fouling on top of trench) |  |  |  |

Notes:

- This Checklist shall be used for IFC Civil foundation drawing review. This review is to check consistency between approved Vendor GAD/Foundation drawing and Civil Foundation drawing issued for construction (IFC).

- Intention of this final review is to address any last-minute misses before actual foundation is casted at site.

- This review shall be done for all foundation mounted mechanical equipment (Pumps, Compressors, GTGs, Vessels, Columns, Exchangers, Packages, etc.)  and Vessel/Sump mounted Pumps.

- This checklist is no way comprehensive. Based on specific project conditions/equipment some points as deemed necessary can be added / deleted. Addition / deletion of points, if any, needs to be taken up in consultation with Lead Engineer / Technical Specialist / Discipline Manager.

- If     is not filled against any item, please indicate N/A or else provide remarks.

- After release of the respective documents, the completed check list shall be retained by Discipline Engineer for future reference and for technical / quality audit.

- Check points shall be filled by job engineer and checked/approved by Lead/Tech. Specialist.

- The final approved Checklist shall be attached with the respective document if required.

| REV. | SIGN | DATE | SIGN | DATE | REMARKS |
| --- | --- | --- | --- | --- | --- |
|  | JOB ENGINEER |  | LEAD ENGINEER |  |  |