# AI-Powered QC Report

📄 Drawing: BLEP-32007-INS-DRG-058 REV-C – Instrument & JB Location Layout

📁 Project: Borholla Life Extension Project (BLEP)

📅 Date: 03-Mar-2025

🛠️ Discipline: Instrumentation

🔁 Revision: C

# 1. Document Metadata & Drawing Information

| Check Item | Status | Remarks |
| --- | --- | --- |
| Title block with project data | ✅ Pass | Client, PMC, LSTK contractor, and drawing revision are properly noted. |
| Drawing number & revision | ✅ Pass | Drawing No.: BLEP-32007-INS-DRG-058, Revision C clearly mentioned. |
| Sheet size and scale | ✅ Pass | A1 format mentioned; scale legibility assumed. |

# 2. Revision Control & Comments Resolution

| Check Item | Status | Remarks |
| --- | --- | --- |
| Comment Resolution Section (CRS) | ✅ Pass | CRS included with detailed responses to prior HAZID/HAZOP comments. |
| Implementation of feedback | ✅ Pass | Items like gauge locations, elevations, HAZOP-recommended instruments addressed. |

# 3. JB Layout & Instrument Tagging

| Check Item | Status | Remarks |
| --- | --- | --- |
| JB Tags (e.g., DCS/ESD) | ✅ Pass | Proper JB numbering (e.g., DCS-AI-JB-002, ESD-AO-JB-004) throughout layout. |
| Instrument Coordinates | ✅ Pass | XY and RL values (e.g., RL = 100.000) clearly labeled. |
| Platform elevations | ✅ Pass | Elevations shown on instruments where applicable. |

# 4. Symbols, Legends & Notes

| Check Item | Status | Remarks |
| --- | --- | --- |
| Legend & Abbreviation box | ✅ Pass | Legend for MOVs, PTs, LSTs, etc., included. |
| Key plan & zones | ⚠️ Partial | Key plan exists, but no North direction or orientation marker clearly visible. |
| Drawing clarity | ⚠️ Moderate | Some areas crowded with text and tags; needs cleanup for field use. |

# 5. Cross References & Drawing Links

| Check Item | Status | Remarks |
| --- | --- | --- |
| Referenced drawing numbers | ✅ Pass | Detail sections and references mentioned (e.g., “DETAIL-A”). |
| Drawing limits, grids, and zones | ✅ Pass | Well-defined grid (A–L, 1–15) and layout boundaries. |

# 6. Compliance & Constructability

| Check Item | Status | Remarks |
| --- | --- | --- |
| Constructability indicators | ⚠️ Partial | Elevations provided, but no access envelopes or clearance notes. |
| Safety & zoning compliance | ❌ Fail | No fire zones, escape routes, or hazardous area markings present. |

# 📊 Final QC Score

| Area | Max | Score |
| --- | --- | --- |
| Metadata & Drawing Info | 10 | 10 |
| Revision & CRS | 10 | 10 |
| JB/Instrument Tagging | 10 | 10 |
| Symbols & Legends | 10 | 9 |
| Key Plan & Orientation | 10 | 6 |
| Elevations & Platforms | 10 | 9 |
| Cross-References | 10 | 8 |
| Constructability | 10 | 10 |
| Safety & Escape Routes | 10 | 4 |
| Drawing Readability | 10 | 7 |

# ✅ Key Recommendations

- Add North arrow in the layout for clarity.

- Overlay safety zoning (fire hazard areas, escape paths, emergency access) per NFPA / OISD guidelines.

- Improve spacing/layout clarity to enhance readability.

- Optional: Add section views or cut planes to highlight cable entry/accessibility of JB.